# Text boxes

Alarm Codes

Room Air Conditioner range:

Indoor unit alarm codes

If timer lamp ﬂashes for 1 second on, 1 second off, this indicates

pre heating on the coil during heating mode and is not an error.

If timer lamp ﬂashes for a number of times and then pauses,

please reference table below. Display will ﬂash as shown in diagram.

LED 301

Range:

Indoor coil is too warm in cooling mode or too cold in heating mode.

Reversing valve or coil thermistor is faulty

Forced operation from the outdoor unit.

This is not an error

Communication error.

Faulty wiring, indoor or outdoor PCB faulty

Outdoor unit fault.

Float switch activated.

Check pump operation and drain

Drain pump forced operation.

Drain test switch in test position, faulty PCB

Louvre not opening.

Louvre motor faulty, microswitch faulty, PCB faulty (RAF unit only)

Faulty indoor unit thermistor.

Air inlet or coil thermistor not connected, open or short circuited faulty PCB

Indoor fan motor over current or abnormal rotation speed.

Faulty motor or PCB

Eprom data error.

Faulty PCB

01

02

03

04

06

07

08

09

10

13

Room Air Conditioner range:

Outdoor unit alarm codes

LED 301

Range:

Normal, unit powered up

Over current on the compressor

Faulty PCB or locked compressor

Over current on the compressor

System power module or PCB failure

Compressor rotation speed is low, abnormal compressor rotor position

Faulty system power module, faulty compressor or PCB

Switching failure on the compressor

Faulty system power module, faulty compressor or PCB

Compressor rotation low with over current detected

High pressure detected, faulty fan motor/circuit or abnormally low voltage

Discharge thermistor temperature rising

Short of refrigerant charge, faulty thermistor, faulty compressor faulty fan motor/circuit or main PCB

1

2

2

with LED302 lit

3

4

5

6

7

8

9

10

12

13

14

Compressor not accelerating above minimum rotation speed

Short of refrigerant charge or faulty compressor

Communication error

C/D terminals not connected, faulty interconnecting cable PCB failure (Summit and Monozone only)

Abnormal voltage

Mains voltage incorrect or faulty reactor

Fan motor rotation is abnormal

Faulty fan motor or PCB (check fuse)

Eprom error

Main PCB failure

Over voltage is detected by system power module

Faulty SPM

If indoor unit ﬁlter lamp is ﬂashing four times, this indicates an

outdoor unit fault. This is identiﬁed by the number of ﬂashes on

LD 301, please see the table right.

If LD 303 is on permanently this is normal operation. If LD 301 is

lit in conjunction with LD 303 this indicates an overload (1)

condition but not an alarm. If LD 302 is lit in conjunction with LD

303 this indicates an overload (2) condition but not an alarm and if

LD 301 and LD 302 are lit in conjunction with LD 303, this indicates

an overload (3) condition but not an alarm.

On Multizone systems only, if LD 301 is lit permanently and LD

302 is ﬂashing a number of times, this indicates a thermistor fault.

Please refer to the table right for the thermistor that is faulty.

If LD 304 is ﬂashing, the number of ﬂashes indicates a

communication error with the corresponding indoor unit circuit

number. Check cable connections, cable is not short circuited

or open circuit and PCB operation.

LD 302

Flashes

1

2

3

4

5

6

7

8

9

Thermistor that is faulty

Compressor overheat (OH)

Defrost thermistor

Ambient thermistor

Narrow pipe (expansion) thermistor, for circuit 1

Wide pipe (suction) thermistor, for circuit 1

Narrow pipe (expansion) thermistor, for circuit 2

Wide pipe (suction) thermistor, for circuit 2

Narrow pipe (expansion) thermistor, for circuit 3

Wide pipe (suction) thermistor, for circuit 3

Indoor unit alarm codes

If run lamp ﬂashes for two seconds on, two seconds off, there is a

failure in the communication between indoor unit PCB and controller.

Causes - open or short circuit on wiring, faulty controller or faulty PCB.

If run lamp ﬂashes once per second and displays alarm code please

reference table below. Display will ﬂash as shown in diagram.

Alarm

code

Category of

failure

Range

Set Free

IVX Systems

Utopia ES

01

02

03

04

Indoor unit

Outdoor unit

High pressure trip (41.3bar)

High pressure trip

(41.3bar) or phase

reversal

High pressure trip

(41.3bar) or phase

reversal

Communication error between indoor and outdoor units. Problem with the communication cable,

power to indoor or outdoor unit, dipswitch settings or PCB

Communication

error

Communication error between outdoor unit main PCB and Inverter PCB. Problem with cables between

the 2 PCBs, power to the inverter PCB or failure of the PCB

Communication error between outdoor unit main PCB and fan PCB. Problem with

the cables between the 2 PCBs, power to the fan PCB or failure of the fan PCB

Phase failure or reversal

Power supply

N/A

N/A

04.

05

06

06.

07

08

09

11

12

13

14

19

Indoor unit

Outdoor unit

Voltage drop to inverter compressor. Problem with mains voltage, capacitors to inverter compressor or

inverter electronics

Voltage drop to condenser fan inverter. Problem with mains voltage, capacitors to inverter fan or

inverter fan electronics

Refrigerant

cycle

Decrease in discharge gas superheat. Excessive refrigerant, indoor expansion valve locked open

(cooling), outdoor expansion valve locked open (heating) or short cycling of air to the indoor unit

Increase of compressor temperature. Shortage of refrigerant, blockage in refrigerant cycle, outdoor

expansion valve locked closed (heating), indoor expansion valve locked closed (cooling)

N/A

Inlet air thermistor alarm. Problem with the connection of the thermistor to the PCB, thermistor open or

short circuit or PCB failure

Outlet air thermistor alarm. Problem with the connection of the thermistor to the PCB, thermistor open

or short circuit or PCB failure

Freeze protection (liquid line) air thermistor alarm. Problem with the connection of the thermistor to the

PCB, thermistor open or short circuit or PCB failure

Gas pipe (suction) thermistor alarm. Problem with the connection of the thermistor to the PCB,

thermistor open or short circuit or PCB failure

Fan motor alarm. Thermal overload on AC fan motors or over/under current/rotation on DC fan motors

System Free

Indoor unit alarm codes

Alarm

code

Category of

failure

Range

Set Free

IVX Systems

Utopia ES

20

N/A

Compressor/discharge gas thermistor

alarm. Problem with the connection of the

thermistor to the PCB, thermistor open or

short circuit or PCB failure

N/A

21

Outdoor unit

22

Discharge pressure transducer alarm. Problem with the

connection of the transducer to the PCB, transducer

open or short circuit or PCB failure

Ambient air thermistor alarm. Problem with the connection of the thermistor to the PCB, thermistor

open or short circuit or PCB failure

Compressor/discharge gas thermistor alarm. Problem

with the connection of the thermistor to the PCB,

thermistor open or short circuit or PCB failure

N/A

23

24

Evaporation thermistor alarm. Problem with the connection of the thermistor to the PCB, thermistor

open or short circuit or PCB failure

FSVNE only. Suction gas thermistor alarm. Problem with

the connection of the thermistor to the PCB, thermistor

open or short circuit or PCB failure

Suction pressure transducer alarm. Problem with the

connection of the transducer to the PCB, transducer

open or short circuit or PCB failure

Incorrect H-LINK wiring. 2 CH boxes are wired in series

Incorrect capacity code setting. Indoor units connected

are more than 130% or less than 50%

N/A

26

Outdoor unit

29

N/A

30

31

32

System

35

36

38

39

41

N/A

Indoor and outdoor unit capacity does not

match

Loss of other unit communication on the same refrigerant cycle number. Other indoor unit switched off,

Communication wiring error, PCB failure on other unit on the same refrigerant cycle number

Duplication of indoor or outdoor unit address on the same H-LINK

Indoor/Outdoor unit combination is not compatible

Abnormality in protection circuit on the outdoor unit. Incorrect connection to outdoor PCB, failure of PCB

Fixed speed compressor over current or under current

N/A

N/A

Outdoor pipe thermistor is over 55oC and

compressor temperature is over 95oC

(cooling mode)

Indoor freeze protection (liquid) thermistor

is over 55oC and compressor temperature

is over 95oC (cooling mode)

N/A

N/A

N/A

Excessively low evaporating temperature

(-35oC)

42

N/A

Pressure ratio falling, protection. Discharge and suction

pressures too close. Check refrigerant charge, failure of

pressure transducer, compressor failure

High suction gas pressure protection

High discharge gas pressure protection

Low suction pressure protection. Restriction or

shortage of refrigerant

43

44

45

47

Pressure

System Free

Indoor unit alarm codes

Alarm

code

Category of

failure

Range

Set Free

IVX Systems

Utopia ES

48

Abnormality of inverter current sensor. Failure of sensor

or inverter PCB

Inverter

Over current on inverter compressor. Failure of

electronics or seized compressor

IPM protection. Over current, low voltage or overheating

Over current detected. Failure of IPM,

PCB2, locked compressor or abnormally

high discharge pressure

Abnormality of inverter current sensor.

Failure of Main PCB, IPM or PCB2

51

52

53

54

55

56

57

58

61

96

KPI thermistor

97

dd

EE

Central station

Outdoor fan

Controller

IPM or PCB2 protection. Over current or

overheating

As Set free, with possibility of outdoor fan

abnormality

Short circuit on remote controller wiring, failure of controller or failure of indoor unit PCB

Abnormality of fan motor position. Transmission failure

on inverter fan motor

Fan controller protection. Abnormal fan speed

Abnormality of fan controller. Over current or over

N/A

Fan motor abnormality. Wiring error between

main and fan PCB or fan motor failure

N/A

Loss of communication of unit, previously detected.

Power to indoor unit, Communication wiring error, PCB failure

Total heat exchanger room temperature thermistor error. Problem with the connection of the thermistor to

the PCB, thermistor open or short circuit or PCB failure

Total heat exchanger outdoor temperature thermistor error. Problem with the connection of the thermistor

to the PCB, thermistor open or short circuit or PCB failure

System

Incorrect communication cable wiring. Crossed with remote controller or crossed on CH box

System locked out due to outdoor unit alarm reset 3 times in 6 hours