# Text boxes

1

RAC Fault Codes

A summary of the fault codes is given in the table below, but they are

described in greater detail in the pages that follow.

Error

Code

Flashing

Lights

Fault

Display

Indoor

Outdoor

Indoor

operation

C1

CH1

C2

CH2

C4

CH4

C5

CH5

C6

CH6

C7

CH7

C8

CH8

C9

CH9

CA

or

or

0r

or

or

or

or

or

1

2

4

5

6

7

8

9

10

Indoor temperature sensor

open or closed circuit

Outdoor temperature sensor

open or closed circuit

Heat sink temperature sensor

open or closed circuit

Communication between indoor

and outdoor units

Excessive current at inverter

DC power circuit

Excessive compressor current

Indoor fan not rotating

Outdoor fan not rotating

1. Discharge temp more than

130 0C

2. Faulty discharge thermistor

EEPROM error

Inverter module error

System in Power Mode – not a

fault

System in test mode – not a

fault

O

O

O

O

O

O

O

O

O

O

O

O

O

O

O

O

ON

ON

ON

OFF

SHUT

DOWN

SHUT

DOWN

OFF

OFF

ON

CC

CD

CE

Po

Lo

2+1

3+1

4+1

O

O

O

O

O

ON

ON

ON

Notes:

On models with an alpha-numeric display the error codes are as per the left hand

column above.

On other models the fault is determined by counting the number of flashes on one or

two led’s. There is an interval of three seconds between repeats of the flashing

sequence.

RAC units for Installation and service engineers

LGEUK July 2007

2

Fault code C1, CH1 or 1 flash

Is a fault with the Indoor unit return air Thermistor

Unplug the Thermistor from the PCB and Check its resistance check against this

graph:

Resistance of air thermistor

0

Temperature deg C

Alternatively the sensor can be tested while still connected to the PCB measure the

DC voltage across the resistor and check it against the graph below.

Voltage across air thermistor

5

Temperature deg C

RAC units for Installation and service engineers

LGEUK July 2007

0

0

5

5

0

0

5

5

0

0

5

5

0

0

5

5

0

0

5

5

0

2

0

0

5

5

4

3

5

t

e

r

m

i

t

r

0

0

s

R

e

s

0

t

n

0

e

k

h

0

0

V

o

l

s

D

C

a

c

r

o

s

s

3

Fault code C2, CH2 or 2 flashes

Is a problem with the Indoor unit coil Thermistor

Unplug the Thermistor from the indoor PCB and Check its resistance against this

graph:

Coil thermistor resistance

0

Alternatively the sensor can be tested while still connected to the PCB measure the

DC voltage across the resistor and check it against the graph below.

Voltage across coil thermistor

5

O

h

3

5

4

5

RAC units for Installation and service engineers

LGEUK July 2007

0

0

0

0

C

0

0

C

0

0

0

0

0

0

5

R

1

si

5

t

n

2

0

0

5

h

0

5

5

e

s

0

t

n

k

O

4

Fault Code C4, CH4 or 4 flashes

Is a fault with the Outdoor unit inverter Heat sink Thermistor, the fault will occur if the

sensor is faulty or the heat sink temperature exceeds 85ºC ?

Unplug the Thermistor from the PCB and Check its resistance check against this

graph (the air thermistor and heat sink thermistor have the same calibration graph)

Resistance of air thermistor

0

Temperature deg C

Alternatively the sensor can be tested while still connected to the PCB measure the

DC voltage across the resistor and check it against the graph below.

Voltage across air thermistor

5

Temperature deg C

RAC units for Installation and service engineers

LGEUK July 2007

0

0

5

5

0

0

5

5

0

0

5

5

0

0

5

5

0

0

5

5

0

2

5

5

5

4

3

0

0

t

e

r

m

i

t

r

0

0

s

0

n

0

s

0

0

V

o

l

s

D

C

a

c

r

o

s

s

t

h

e

k

e

5

Fault code C5, CH5 or 5 flashes

This fault code indicates a communication error between the indoor and outdoor units.

If there is a communication error fault CH05, will appear within 5 minutes of powering

up the system.

Communications between the outdoor and indoor units are via terminal 3 and N of

the interconnecting cable. Communications errors can be due to:

1. Cable and cable connection faults.

2. Devices such as an external pump connected to the communications

terminals

3. Faulty indoor or outdoor PCBs.

If there is a communications error CH05, then first check the terminals at both the

indoor and outdoor units for any devices other than the interconnecting cable.

Remove such equipment, and connect them elsewhere. If the fault persists, proceed

as follows:

1. Disconnect the signal cable at both ends (Terminal 3).

2. With the INDOOR unit powered up and switched on, check the DC voltage at

the INDOOR unit between the signal (terminal 3) and neutral. Connect the red

lead from your meter to 3 and the Black lead to N, the Voltage should be

negative, and fluctuating up to about -70 V. If there is no voltage, the indoor

PCB is faulty

3. With the OUTDOOR unit powered up and switched on, check the DC voltage

at the OUTDOOR unit between the signal (terminal 3) and neutral, connect

the red lead from your meter to 3 and the black lead to N, It should be positive,

fluctuating up to about +70 V. If there is no voltage, the outdoor PCB is faulty

4. If the tests in 2 and 3 above show the correct voltage, the fault lies in the

interconnecting cable. Remove all cores at both ends, and check for open

and short circuits, including shorts to earth. Check also that there are no

switches on the signal wire, since poor contact can cause the problem. Check

also that there are adequate earth connections at both the indoor and outdoor

units.

5. When communications are healthy, there should be up to +70V DC between

the signal and neutral wires when the unit is running and the interconnecting

cable is connected.

Fault code C6, CH6 or 6 flashes

This fault is caused by an over current in the inverters DC power circuit. This is

caused by either the inverter PCB or compressor being short circuit or down to earth.

Check the resistance of the compressor windings with the electrical connections

disconnected, typically they should be between 1 and 5 Ohms each.

If the compressor is OK check the inverter output voltages are all equal.

Fault Code C7, CH7 or 7 flashes

This fault is caused by a Compressor over-current see code 06

RAC units for Installation and service engineers

LGEUK July 2007

6

Fault Code C8, CH8 or 8 flashes

This fault is caused by the Indoor fan being locked;

Check the fan motor is plugged into the indoor PCB correctly; check the fan motor is

turning, if not check the AC Voltage supplied to the fan motor, this will vary from 120

V ac at low speed to 170V AC at high speed.

If no Voltage is present the PCB is faulty, if the Voltage is present the fan motor will

be Faulty.

Fault Code C9, CH9 or 9 flashes

This is an Outdoor unit fan motor fault

Check the fan motor is plugged into PCB correctly; Start the unit up the fan motor

should turn when the compressor is running.

Check the fan motor is turning, if not check the Voltages supplied to the fan motor,

there will be a connector on the PCB with five wires, measure from red to Black, it

should be 300 - 320V DC,

From white to Black it should be 10-15V DC,

If no Voltage is present the PCB is faulty, if the Voltage is present the fan motor will

be Faulty.

Fault Code CA or 10 flashes

This fault is caused by the compressor discharge sensor reading over 130ºC or the

discharge Thermistor being faulty.

Reset the power, if the fault goes away and the compressor starts check the

discharge temperature, if it is very hot check the refrigerant charge. High discharge

temperatures are usually caused by shortage of refrigerant.

If the unit wont restart after resetting the power check the Thermistor, Unplug the

Thermistor from the PCB and Check its resistance check against this graph:

RAC units for Installation and service engineers

LGEUK July 2007

7

Resistance of discharge thermistor

0

0

0

0

e

s

0

t

0

n

0

k

0

h

0

s

0

0

0

0

2

4

V

o

5

t

g

e

6

C

7

9

8

3

Alternatively the sensor can be tested while still connected to the PCB measure the

DC voltage across the resistor and check it against the graph below.

Voltage across discharge thermistor

Fault Code CC or 2 + 1 flashes (2 flashes on one led, 1 flash on another)

Check the correct PCB assembly has been installed, check for dry joints, replace

outdoor unit PCB if nothing is found.

Fault Code CD or 3 + 1 flashes (3 flashes on one led, 1 flash on another)

This fault indicates a problem with the inverter module, see section on testing

inverters. Also check reactor is connected to the PCB and check its resistance it

should be well under 1 Ohm.

RAC units for Installation and service engineers

LGEUK July 2007

0

0

0

0

C

0

0

C

0

0

0

0