# Text boxes

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Universal and Multi Split Units

If there is a fault on any LG Universal or Multi unit, a two digit number will appear on the remote controllers led

display. If the unit does not have a remote controller the fault will be displayed using the LED's on the front of

the indoor unit.

2nd digit

1st digit

The second digit of the fault code is shown by the power led which has the following symbol by it

The first digit will be displayed by one other led.

Error Indicator:









The function provides self-diagnosis and displays an error code if there is any trouble.

Error codes are displayed on the Indoor unit’s Wired Remote as CH**, and/or Fascia Display. In

addition, the code is indicated via LED’s on the outdoor unit control board.

If more than two troubles occur simultaneously, the lower number of error code is displayed first.

After an error occurs, if error is released, error LED is also released simultaneously.

Indoor Unit Faults:

Error

code

01

02

03

04

05

06

07

HL

CL

Po

Contents

Air sensor (open/short)

Inlet pipe sensor

Communication(Indoor ↔ Wired

R/Control)

Drain pump / Float switch

Communication(Indoor ↔ Outdoor)

Outlet pipe sensor

Different operation mode

High Limit (Float Switch)

Child Lock Function selected

Jet Cool Mode selected

Case of error

Open / Short circuit

Open / Short circuit

Communication Poorly

Float switch Open circuit (High level water

alarm)

Communication Poorly

Open / Short circuit

Indoor units set in different operation modes

Same as code 04, Float switch Open circuit

Not an error, press Timer & Min buttons

simultaneously for 3 seconds to toggle On/Off

Not an error, press Jet Cool button to toggle

On/Off

Indoor

Status

Off

Off

Off

Off

Off

Off

Off

Off

On

On

Hendra/Macedo - April 2007

-1-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Outdoor Unit Faults can also be read from the outdoor unit PCB using the flashing LED’s as below:

Error

code

21

22

23

24

25

26

27

28

32

33

40

41

44

45

46

47

48

51

52

53

54

60

61

62

63

65

67

105

LED01G

(Red)

2 times

2 times

2 times

2 times

2 times

2 times

2 times

2 times

3 times

3 times

4 times

4 times

4 times

4 times

4 times

4 times

4 times

5 times

5 times

5 times

5 times

6 times

6 times

6 times

6 times

6 times

6 times

6 times

1 time

2 times

3 times

5 times

7 times

5 times

1 time

4 times

5 times

6 times

7 times

8 times

1 times

2 times

3 times

4 times

LED02G

(Green)

1 time

2 times

3 times

4 times

5 times

6 times

7 times

8 times

2 times

3 times

Off

Off

Off

CT Circuit malfunction

Open / Short circuit.

Open / Short circuit

Open / Short circuit

Open / Short circuit

Open / Short circuit

Dual Sensor unplugged

Over Load Combination

Poor/Loss of Communication

Poor/Loss of Communication

Incorrect Wiring

Check Sum Mis-Match

Cond. Temp. High

Heat Sink Temp. High

Cond. Temp. Low

Open / Short circuit

Fan Motor/Circuit Problem

Poor/Loss of Communication

Outdoor

Status

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Off

Contents

IPM Fault (Compressor Over

current)

CT 2 (Max. Current)

DC Link Low Volt.

Low / High Pressure

AC Low / AC High Volts.

DC Compressor Position

PSC Fault (Reactor)

DC Link High Volts

Discharge Pipe Temp. High (INV)

Discharge Pipe Temp. High

(Cons.)

CT Circuit

D-Pipe sensor INV. (Open/Short)

Air sensor (Open/Short)

Cond. Pipe Sensor (Open/Short)

Suction Pipe Sensor

(Open/Short)

D-pipe Sensor Cons.

(Open/Short)

D-Pipe & Air Sensor (Open)

Over Capacity

Communication Error (Main

micom ↔ Sub micom)

Communication Error (Indoor ↔

Outdoor)

Outdoor 3-Phase Power Supply

Reverse Phase / Missing Phase

EEPROM Check Sum

Cond. Pipe Sensor Temp. High

Heat Sink Sensor Temp. High

Cond. Pipe Sensor Temp. Low

Heat Sink Sensor (Open/Short)

Outdoor BLDC Fan Lock

Comms. Error (Main board ↔Fan

board)

Case of Error

Compressor malfunction, IPM

Fault

Current is 14A ↑

DC Link volt. Is 140V ↓

Low / High press switch

OPEN

Abnormal AC volt. Input.

The codes are explained in detail on the following pages.

Hendra/Macedo - April 2007

-2-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault code 01

Is a fault with the Indoor unit return air Thermistor

Unplug the Thermistor from the PCB and Check its resistance check against this graph:

Resistance of Air thermistor

Resistance

20

18

16

14

12

10

8

6

10

15

20

25

30

35

40

Temperature

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across Air thermistor

3.5

3.0

2.5

2.0

1.5

10

15

20

25

30

35

40

Volts

Temperature

Hendra/Macedo - April 2007

-3-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault code 02

Is a problem with the Indoor unit coil inlet Thermistor

Unplug the Thermistor from the indoor PCB and Check its resistance against this graph:

Coil thermistor resistance k Ohms

20

Resistance

15

10

5

0

0

10

20

30

40

50

60

70

Temperature

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across coil thermistor

4.0

3.0

Volts

2.0

1.0

0.0

0

10

20

30

Temp

40

50

60

70

Hendra/Macedo - April 2007

-4-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 03

Indicates a wiring error between the remote controller and the fan coil, this is most common in group control

applications where more than 1 fan coil is connected to a single remote controller.

Firstly check the wiring has been done correctly see below.

1 2 3

2 3

2 3

Next check the switch in the back of the remote controller, it has to be set to Group or GR1 for group control,

the Factory setting is Single or SG, after setting the switch reset the power for 2 minutes. If the fault does not

clear, check the Voltage of the remote controller cable.

The Red cable is 12 Vdc

The Brown or Black cable is Ground or 0 Vdc

The Yellow is signal (Comms.)

Test

Voltage across the Brown/ Black cable and the Red, this

should be 12 Vdc

Voltage from Yellow to Brown/Black this should be

fluctuating between 8 – 12 Vdc.

Hendra/Macedo - April 2007

-5-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 04

Fault code CH04 indicates that the float switch of the fan coil has risen.

On fan coils without a drain pump it indicates that the jumper (blue plug with 30mm of blue wire) in terminal

CN FLOAT is missing.

If the fan coil is running and the float rises it will take 3 ½ minutes for the fault to show on the controller, this is

to give the unit time to pump excess water away. Once the float falls, (or the jumper is put back into the board)

it will not be possible to clear the fault for 40 seconds. It is considered good practice to reset the power to

clear this fault code.

Fault Code 05

This fault code indicates a communication error between the indoor and outdoor units; this is usually caused

by wiring errors or condensate pumps connected to the inter-connecting cable.

The communication between the units is a fluctuating DC voltage commonly called a serial signal, it can be

easily lost if the wiring is not done correctly. If there is a communication error fault CH05 will appear within 5

mins of powering up the system.

Testing

Turn on the power and start the indoor unit in cooling, set the temperature to 18ºC; the serial communication

signal will only be present for the first 3 mins of operation.

Set your meter to DC Volts, Test between terminals 2 and 3, of the outdoor unit and wiring terminals you

should see 0-65 V dc, it will be fluctuating.

If the Voltage is not present disconnect the inter unit wiring, test the Voltage on the wiring terminals again, If

No Voltage is present the outdoor PCB must be faulty.

Once the signal has been detected leaving the outdoor unit check what is being received by the indoor unit,

measure DC Voltage across the wiring terminal 2 and 3, it should be identical to what you saw at the outdoor

unit, if not your wiring is at fault.

Hendra/Macedo - April 2007

-6-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault code 06

Is a problem with the Indoor unit coil outlet Thermistor

Unplug the Thermistor from the indoor PCB and Check its resistance against this graph:

Coil thermistor resistance k Ohms

20

Resistance

15

10

5

0

0

10

20

30

40

50

60

70

Temperature

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across coil thermistor

4.0

3.0

Volts

2.0

1.0

0.0

0

10

20

30

Temp

40

50

60

70

Hendra/Macedo - April 2007

-7-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 07

On Multi split systems, the first unit switched on is the cool heat master, the master tells the condensing unit

what to do. If the condenser is in heating and any slave is set to cooling a CH07 fault code will appear.

Likewise if the condenser is in cooling and any slave is set to heating a CH07 fault code will appear. If the

master is switched off the next longest running unit becomes the master.

To clear the fault turn off the unit at the remote controller, turn it back on again and change the mode

Fault Code 21

This fault is caused by an over current in the inverters DC power circuit. If the DC part of the circuit exceeds

14 Amps fault code 21 will be displayed.

This is caused by either the inverter PCB being faulty or compressor being short circuit or down to earth.

Disconnect the electrical connections to the compressor and check

the resistance of the compressor windings, measure from U to V, V

to W and W to U the values should be between 0.25 and 5 Ohms

each.

The next test is to measure the resistance of the compressor

windings to earth.

Using a Megger (High Voltage Meter) measure the resistance from

any of the 3 compressor terminals to an Earth point (pipe work).

The value should exceed 2 M Ohms.

If the compressors fail these tests it will need replacing.

If the compressor is OK you will need to check the inverter output voltages. Please see section on Inverter

testing at end.

Fault Code 22

This fault is caused by a Compressor over-current see code 21

Please see section on Inverter testing at the end.

Fault Code 23

This fault indicates a fault in the DC part of the inverter circuit; it means that the Dc Voltage to the inverter is

below 140 V Dc, it should be 370 V for single phase machines and 600 V dc for three phase machines. The

fault is usually caused by the inverter charging resistor being faulty; this component is mounted on the outdoor

unit PCB and cannot be replaced.

Start the unit running and measure the DC Voltage supply to the inverter. This is easiest to measure at the

inverter capacitors; it should be 370 V for single phase machines and 600 V dc for three phase machines

See section on Inverter testing at the end.

Hendra/Macedo - April 2007

-8-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 24

If the unit has a low or high pressure fault CH24 will display.

If the LP switch goes open circuit the compressor will be stopped, on inverter units this can take up to 30

seconds. The LP Switch goes open circuit when the suction pressure falls below 0.5 bar the Hp Switch opens

at 41 bar.

The fault code will only occur if the pressure switch is tripped 5 times within 1 hour, this can only be reset by

switching off the power to the condensing unit for 2 minutes.

If your unit does not have any pressure switches it may still have a plug on the outdoor unit PCB labelled CN

Press, it should have a link plugged in, if the link is missing it must be replaced.

Fault Code 25

This fault indicates a problem with the incoming power supply to the system.

Measure the Voltage of the incoming supply, if it is less than 140V AC or greater than 300V AC this fault will

occur.

If the Power supply is correct and the fault persists replace the outdoor unit PCB.

Fault Code 26

This fault indicates a problem with the positioning system of the inverter compressor, which indicates a seized

compressor.

Firstly check the compressor is correctly connected. Next reset the power supply to the system ensuring the

power is left off for 5 minutes. Start the unit up, after a couple of minutes the compressor will try and start, you

can hear a high pitched whine when it does. If the compressor does not start turning within a couple of

seconds the whining will stop. The compressor will try to start 3 times then the fault will recur.

Fault Code 27

This fault indicates a problem with the inverter module, see section on testing inverters. Also check reactor is

connected to the PCB and check its resistance it should be well under 1 Ohm.

Fault Code 28

This fault indicates a problem in the DC part of the inverter circuit; it means that the DC Voltage to the inverter

is too high.

Start the unit running and measure the DC Voltage supply to the inverter. This is easiest to measure at the

inverter capacitors; it should be 370 V for single phase machines and 600 V dc for three phase machines. See

section on Inverter testing at end.

Fault Code 32

Indicates that the Inverter compressor discharge temperature is high (above 105ºC) this usually indicates the

system has either a shortage of refrigerant or a blockage in the system.

Reset the power to the unit for 2 minutes and restart it. If the compressor starts measure the compressor

discharge temperature, typically it should not be more than 50ºC above the ambient temperature around the

condensing unit. It may take quite a long period for the compressor to overheat so don’t just start the unit and

run. Make sure you check the unit is operating correctly and providing adequate cooling.

Hendra/Macedo - April 2007

-9-

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 33

Indicates that the fixed speed compressor discharge temperature is high (above 105ºC) this usually indicates

the system has either a shortage of refrigerant or a blockage in the system.

Reset the power to the unit for 2 minutes and restart it, If the compressor starts measure the compressor

discharge temperature, typically it should not be than 50ºC above the ambient temperature around the

condensing unit. It may take quite a long period for the compressor to overheat so don’t just start the unit and

run. Make sure you check the unit is operating correctly and providing adequate cooling.

Fault Code 40

This fault indicates a problem with the current drawn by the AC part of the inverter circuit.

Refer to the inverter testing procedure at the end.

Hendra/Macedo - April 2007

- 10 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 41

This fault indicates an Inverter Compressor discharge Thermistor fault

Unplug the Thermistor and Check its resistance check against this graph:

Resistance of discharge pipe thermistor

250

resistance

200

150

100

50

0

20

30

40

50

60

70

80

90

100

110

temp

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across discharge thermistor

5.0

4.5

4.0

3.5

3.0

2.5

2.0

1.5

1.0

20

30

40

50

60

70

80

90

100

110

Voltage

Temp

Hendra/Macedo - April 2007

- 11 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 44

Indicates a fault with the Outdoor unit air Thermistor

Unplug the Thermistor from the PCB and Check its resistance check against this graph:

Resistance of Air thermistor

Resistance

20

18

16

14

12

10

8

6

10

15

20

25

30

35

40

Temperature

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across Air thermistor

3.5

3.0

2.5

2.0

1.5

10

15

20

25

30

35

40

Volts

Temperature

Hendra/Macedo - April 2007

- 12 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 45

Indicates a problem with the condenser coil outlet Thermistor

Unplug the Thermistor from the indoor PCB and Check its resistance against this graph:

Coil thermistor resistance k Ohms

20

Resistance

15

10

5

0

0

10

20

30

40

50

60

70

Temperature

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across coil thermistor

4.0

3.0

Volts

2.0

1.0

0.0

0

10

20

30

Temp

40

50

60

70

Hendra/Macedo - April 2007

- 13 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 46

Indicates a problem with the compressor suction Thermistor

Unplug the Thermistor from the indoor PCB and Check its resistance against this graph:

Coil thermistor resistance k Ohms

20

Resistance

15

10

5

0

0

10

20

30

40

50

60

70

Temperature

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across coil thermistor

4.0

3.0

Volts

2.0

1.0

0.0

0

10

20

30

Temp

40

50

60

70

Hendra/Macedo - April 2007

- 14 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 47

Indicates an Inverter Compressor discharge Thermistor fault

Unplug the Thermistor from the PCB and Check its resistance check against this graph:

Resistance of discharge pipe thermistor

250

resistance

200

150

100

50

0

20

30

40

50

60

70

80

90

100

110

temp

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across discharge thermistor

5.0

4.5

4.0

3.5

3.0

2.5

2.0

1.5

1.0

20

30

40

50

60

70

80

90

100

110

Voltage

Temp

Hendra/Macedo - April 2007

- 15 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 48

This fault indicates that the compressor discharge sensor and the condenser air temperature sensors are both

unplugged. Both these sensors are connected to a single connector on the outdoor unit PCB, plug it in and

the fault will go away.

Fault Code 51

This indicates that the capacity of the indoor unit / units is too great for the condensing unit. Make a note of

the model number of the fan coil/coils and the condensing unit and check with the equipment supplier that the

units you have installed can be connected together.

Fault Code 52

This fault code indicates a communication error between the Main and Sub micom (CPU’s) on the outdoor

unit main PCB. Check for evidence of damage, if none found reset power, if fault reappears replace pcb.

Fault Code 53, (see fault code 05)

Fault Code 54

This fault normally indicates a lost phase or the phases are reversed on the power supply to 3 phase units.

Check all 3 phases are available at the power terminals to the unit. You should have 415v AC across red to

blue, blue to yellow and red to yellow,

If this is all ok turn off the power and swap the red and yellow cores of the power supply cable over, reset the

power and the unit will operate.

Fault Code 60

Check the correct PCB assembly has been installed, check for dry joints, replace outdoor unit PCB if nothing

is found.

Fault Code 61

Indicates the outdoor unit condenser coil temperature is high above 65ºC, this will usually be experienced in

cooling mode and will indicate insufficient air being drawn over the coil.

Check there are no blockages to the coil (carrier bags dirt etc); check the air flow is not short circuiting from

the front to the back of the unit and check for Nitrogen in the system.

Fault Code 62

Indicates the outdoor unit Inverter heat-sink thermistor has detected that the heat sink is overheating 85ºC.

This is usually caused by debris blocking the heat-sink fins or an error with the thermistor, see code 65.

Hendra/Macedo - April 2007

- 16 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 65

Is a problem with the Inverter PCB heat sink thermistor for the heat sink on the outdoor unit PCB, unplug the

Thermistor from the PCB and Check its resistance against this graph:

resistance of Heat sink thermistor

20

Resistance

18

16

14

12

10

8

6

10

15

20

25

Temperature

30

35

40

Alternatively the sensor can be tested while still connected to the PCB measure the DC voltage across the

resistor and check it against the graph below.

Voltage across Heat Sink thermistor

3.5

3.0

Volts

2.5

2.0

1.5

20

25

30

Temperature

35

40

Hendra/Macedo - April 2007

- 17 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Fault Code 67

This is a problem with the Outdoor Fan Motor, where rotation is not detected, and could be result of either

Mechanical or Electrical failure.

 Check that motor is free to rotate and not seized.

 Check the motor is electrically sound, windings not Open or Short circuit.

 Check power output from PCB to fan motor.

 Check rotation feedback circuit.

More modern units use inverter fan motors, which are powered by a DC Voltage.

In reality these fan motors are AC fan motors with a small inverter-type circuit build inside. This inverter circuit

is integrated with the fan motor and impossible to replace, you have to replace the entire fan motor.

Similar to inverter-controlled compressors, the speed of these fan motors can be changed to whatever is

needed (within certain limits). In practice the change in fan speed is not ‘continuous’ but certain fixed speeds

have been programmed inside the AC unit.

This type of fan control can be recognized by the 5 wires coming from the fan on a connector with 7 possible

connections

These fan motors have 5 connections, power supply is 360VDC, and the speed is determined by a voltage

ranging from 0 (0 rpm) to 5VDC (max speed) and a power supply for the internal electronics of 15VDC.

These motors are easy to identify from a wiring diagram, they always show them not connected to anything as

the electronics are too difficult to draw on the diagram.

Detail of Hall Sensors

A Hall effect sensor works like a magnetic reed switch, one end is wired to a 15 Vdc supply and the other is

the feed back to the PCB. As a magnet mounted on the rotor of the motor passes the hall sensor the reed

switch closes momentarily and allows the DC signal to flow through it back to the PCB. The hall sensors have

a resistance so the voltage fed back to the PCB will only be approximately 12V DC.

The pcb will know what speed the fan motor should be turning as it is also controlling the output of the

inverter, if there is a discrepancy between the inverter output RPM and the feedback from the hall sensors a

fault will occur. Usually the fan will rev very fast for a few seconds then stop this indicates hall sensor

problems.

Replace either Motor or Fan PCB as necessary.

Fault Code 105

This is due to a Communication error between the Main outdoor PCB and Fan PCB.







Check for Open/Short of communication line between the Main and Fan PCB’s.

Check communication cable plug connections.

Is the communication LED on?

Hendra/Macedo - April 2007

- 18 -

LG Air Conditioning Universal & Multi Split Fault Codes Sheet

Testing Inverters

It is best to test inverters with no compressors connected especially if you expect the compressor is at fault.

But if you remove the wires from the compressor and try to run the systems a fault will be displayed. The fault

is caused by the inverter PCB being able to detect whether a compressor is connected or not. Most modern

inverters are able to detect whether the compressor has been disconnected in only a few seconds making

testing very difficult.

Testing can be done in two ways:

Firstly the hard way……

You will need a digital multi meter with a min max function,

Turn off the power

Disconnect the compressor either from the PCB or at the compressor terminals.

Connect your meter to two of the phases (Red to blue) set your meter to record max and min voltage

Power up and Start the unit

Let the inverter start and watch the Voltage rise

Record the maximum Voltage

The inverter will stop after a few seconds and the voltage will fall to 0

Swap the leads to measure the next two phases (Red to Yellow).

Measure as before

Repeat for the last two phases Blue to Yellow.

The readings of maximum voltage should be the same for all 3 measurements if not the inverter is faulty, the

PCB will need replacing.

If the readings are equal the Inverter is healthy and the compressor will need replacing.

And the easy way:

You will need an LG Inverter tester,

Turn off the power

Disconnect the compressor lead from the compressor terminals.

Connect your inverter tester to all 3 leads (polarity is not important)

Power up and Start the unit

Let the inverter start and watch the led’s

All 6 must light up and should be of equal brightness

The inverter will stop after a few seconds and the led’s will go out

If you miss the led’s (they will only light for a couple of seconds) the unit will try to start again 3 times with a 3

minute delay between each test

If all 6 led’s DON’T light up the inverter is faulty, the PCB will need replacing.

If the led’s all light up the Inverter is healthy and the compressor will need replacing.

Hendra/Macedo - April 2007

- 19 -